## supply
essentials |  |  |  | costs |  | constraints
|  |  |  | monetary | co2
name | color | parent | carrier_out | om_con | om_con | lifetime
electricity_econatur | #094926 | supply | electricity | 0.2505 | 0.02 | 1
gas_standard | #ffd191 | supply | gas | 0.1325 | 0.23 | 1
pallet | #c4d79b | supply | pallet | 0.102 | 0.028 | 1
oil | #e6b8b7 | supply | oil | 0.1 | 0.324 | 1
district_heating | #219ce1 | supply | DH | 0.122 | 0.051 | 1
Note on E3: Yiqiao Wang: cost of energy usage [$/kWh]
Note on G3: Yiqiao Wang: [year]; if no monetary discount is wanted for future years, set the lifetime to 1.
Note on F5: Yiqiao Wang: kbob
Note on E6: Yiqiao Wang: bfe+wk palletten energie 360 suggests 0.08CHF/kWh on 11.4.2024
Note on F6: Yiqiao Wang: kbob
Note on E7: Yiqiao Wang: 100Fr/100L 10kWh/L
Note on F8: Yiqiao Wang: kbob, between waste water and ground water

## supply_renewable
essentials |  |  |  | costs |  |  | constraints
|  |  |  | monetary |  | co2
name | color | parent | carrier_out | energy_cap | purchase | energy_cap | resource | force_resource | resource_unit | resource_area_per_energy_cap | energy_cap_min | energy_cap_max | lifetime
PV_small | #c69871 | supply_for_pv |  | 3000 | [6 empty] | 1 | 10
PV_middle | #c69872 | supply_for_pv |  | 1600 | [6 empty] | 10 | 100
PV_large | #c69873 | supply_for_pv |  | 1300 | [6 empty] | 100 | 200
PV_extra_large | #c69874 | supply_for_pv |  | 1000 | [6 empty] | 200 | 2000
SCFP | #c4d79b | supply | heat_60 | 1576 | 1 | 290 | df=supply_SCFP | TRUE | energy_per_area | 1.297 | 1 |  | 23
SCET | #e6b8b7 | supply | heat_85 | 2047 | 1 | 296 | df=supply_SCET | TRUE | energy_per_area | 1.41 | 1 |  | 23
Note on E3: Yiqiao Wang: slope of installation cost curve [$/kW]
Note on J3: Yiqiao Wang: Sets the unit of resource to either energy (i.e. kWh), energy_per_area (i.e. kWh/m2), or energy_per_cap (i.e. kWh/kW). energy_per_area uses the resource_area decision variable to scale the available resource while energy_per_cap uses the energy_cap decision variable.
Note on K3: Yiqiao Wang: [m2/kW] If solar radiation is 1000W/m2 and efficiency is 18%, then PV yields 0.18 kW/m2 energy intensity, and this value is (1/0.18)=5.56.
Note on L3: Yiqiao Wang: [kW], minimum technology installation capacity
Note on M3: Yiqiao Wang: [kW], maximum technology installation capacity
Note on N3: Yiqiao Wang: [year]; if no monetary discount is wanted for future years, set the lifetime to 1.
Note on E4: Yiqiao Wang: HSLU
Note on F4: Yiqiao Wang: just adding binary variable to technology. This somehow helps with model feasibility.
Note on G4: Yiqiao Wang: 34.029 from KBOB
Note on E8: Yiqiao Wang: HSLU 1812; SCET generally more expensive (20-40%) and hotter than SCFP; SCFP:1812*0.87; SCET:1812*1.13.
Note on G8: Yiqiao Wang: emission is different in different house sizes
Note on K8: Yiqiao Wang: 1/0.771 from CEA database
Note on N8: Yiqiao Wang: danish solar heating, average single/apart
Note on G9: Yiqiao Wang: based on KBOB data; a bit higher for SCET because of higher value (109) than SCFP (104) on Oekobaudat.
Note on K9: Yiqiao Wang: 1/0.71 from CEA database.
Note on N9: Yiqiao Wang: danish solar heating, average single/apart

## conversion
essentials |  |  |  |  | costs |  |  |  | constraints
[5 empty] | monetary |  |  | co2
name | color | parent | carrier_in | carrier_out | energy_cap | purchase | om_annual | energy_cap | energy_eff | energy_cap_min | energy_cap_max | lifetime
DH_15_50 |  | district_heating_techs |  |  | 371.8 | 7323 |  |  |  | 15 | 50
DH_50_200 |  | district_heating_techs |  |  | 180.88 | 16869 |  |  |  | 50 | 200
DH_200_500 |  | district_heating_techs |  |  | 117.4 | 29571.7 |  |  |  | 200 | 500
DH_500_2000 |  | district_heating_techs |  |  | 72.01 | 52250 |  |  |  | 500 | 2000
ASHP_35 |  | ASHP |  | heat_35 |  |  |  |  | 4.58
GSHP_35 |  | GSHP |  | heat_35 |  |  |  |  | 7.64
ASHP_60 |  | ASHP |  | heat_65 |  |  |  |  | 2.89
GSHP_60 |  | GSHP |  | heat_65 |  |  |  |  | 4.13
ASHP_85 |  | ASHP |  | heat_85 |  |  |  |  | 2.2
GSHP_85 |  | GSHP |  | heat_85 |  |  |  |  | 2.96
gas_boiler_small |  | gas_boiler |  |  | 300 | 17200 |  |  |  | 1 | 20
pallet_boiler_small | #c4d79b | pallet_boiler |  |  | 880 | 25100 |  |  |  | 1 | 20
oil_boiler_small | #e6b8b7 | oil_boiler |  |  | 486.7 | 20466.7 |  |  |  | 1 | 20
gas_boiler_middle |  | gas_boiler |  |  | 176.7 | 19666.7 |  |  |  | 20 | 200
pallet_boiler_middle | #c4d80b | pallet_boiler |  |  | 415 | 34400 |  |  |  | 20 | 200
oil_boiler_middle | #e6b8b8 | oil_boiler |  |  | 189.4 | 26411.1 |  |  |  | 20 | 200
gas_boiler_large |  | gas_boiler |  |  | 155.3 | 23933.3 |  |  |  | 200 | 500
pallet_boiler_large | #c4d81b | pallet_boiler |  |  | 278 | 61800 |  |  |  | 200 | 500
oil_boiler_large | #e6b8b9 | oil_boiler |  |  | 211.7 | 21966.7 |  |  |  | 200 | 500
HEX_85_60 |  | conversion | heat_85 | heat_60 |  |  |  |  | 1 |  |  | 1
HEX_60_35 |  | conversion | heat_60 | heat_35 |  |  |  |  | 1 |  |  | 1
Note on F3: Yiqiao Wang: slope of installation cost curve [$/kW]
Note on G3: Yiqiao Wang: interception of installation cost curve [$/device]
Note on H3: Yiqiao Wang: maintenance [CHF/kW/year]
Note on J3: Yiqiao Wang: efficiency of conversion technology
Note on K3: Yiqiao Wang: [kW], minimum technology installation capacity
Note on L3: Yiqiao Wang: [kW], maximum technology installation capacity
Note on M3: Yiqiao Wang: [year]; if no monetary discount is wanted for future years, set the lifetime to 1.
Note on A4: Yiqiao Wang: ewz
Note on I4: Yiqiao Wang: from Oekobaudat 1kW district heating station, 1kW/kg: 4.771 kgCO2eq/kg
Note on A8: Yiqiao Wang: here, ASHP cannot work reversely and create cooling. Addition chiller should be added to the system.
Note on F8: Yiqiao Wang: HSLU, 2024
Note on H8: Yiqiao Wang: HSLU with no interception
Note on J8: Yiqiao Wang: carnot efficiency 52% reference point temperature 0degC
Note on M8: Yiqiao Wang: 16-20, Danish energy agency
Note on J9: Yiqiao Wang: carnot efficiency 62%, Danish 35degC high temp, 10degC low temp (in the ground)
Note on F10: Yiqiao Wang: HSLU, 2024
Note on H10: Yiqiao Wang: HSLU with no interception
Note on M10: Yiqiao Wang: 16-20, Danish energy agency
Note on J11: Yiqiao Wang: 60/10
Note on F12: Yiqiao Wang: HSLU, 2024
Note on H12: Yiqiao Wang: HSLU with no interception
Note on M12: Yiqiao Wang: 16-20, Danish energy agency
Note on F14: Yiqiao Wang: HSLU, piecewise
Note on H14: Yiqiao Wang: HSLU, no interception allowed for maintenance in Calliope
Note on I15: Yiqiao Wang: pallet boiler 14.9kW from Oekobaudat
Note on H17: Yiqiao Wang: HSLU, no interception allowed for maintenance in Calliope
Note on I18: Yiqiao Wang: pallet boiler 20-120kW Oekobaudat
Note on H20: Yiqiao Wang: HSLU, no interception allowed for maintenance in Calliope
Note on I21: Yiqiao Wang: pallet boiler 20-120kW Oekobaudat
Note on M23: Yiqiao Wang: hypothetical technology to cool down the water, no need to set up cost or emission

## conversion_plus
essentials | [8 empty] | costs | [6 empty] | constraints
[9 empty] | monetary |  |  |  |  | co2
name | color | parent | carrier_in | carrier_in_2 | primary_carrier_in | carrier_out | carrier_out_2 | primary_carrier_out | energy_cap | interest_rate | export | purchase | om_annual | energy_cap | interest_rate | energy_eff | carrier_ratios |  |  | export_carrier | energy_cap_min | energy_cap_max | lifetime
[17 empty] | carrier_in_2 |  | carrier_out_2
[17 empty] | heat_35 | heat_60 | electricity
gas_micro_CHP |  | conversion_plus | gas |  |  | heat | electricity | heat | 1108.2 | 0.05 | -0.1272 | 33195 | 1.15 | 86.82 | 0 | 0.55 |  |  | 0.64 | electricity | 10 | 500 | 15
Note on J3: Yiqiao Wang: slope of installation cost curve [$/kW]
Note on M3: Yiqiao Wang: interception of installation cost curve [$/device]
Note on N3: Yiqiao Wang: maintenance [CHF/kW/year]
Note on Q3: Yiqiao Wang: efficiency of conversion technology
Note on R3: Yiqiao Wang: please refer to https://calliope.readthedocs.io/en/stable/user/advanced_constraints.html#the-conversion-plus-tech for detailed documentation.
Note on V3: Yiqiao Wang: [kW], minimum technology installation capacity
Note on W3: Yiqiao Wang: [kW], maximum technology installation capacity
Note on X3: Yiqiao Wang: [year]; if no monetary discount is wanted for future years, set the lifetime to 1.
Note on R5: Yiqiao Wang: levels labelled in red are technology-specific!
Note on T5: Yiqiao Wang: Here, electricity's output ratio (relative to heat output) is defined, because 1 portion of gas can produce 0.55 portion of heat and 0.35 portion of electricity. 0.35/0.55=0.64. In other words, the efficiency of electricity production from gas would be: energy_eff*carrier_ratios.carrier_out_2.electricity =0.55*0.64=0.35. Same applies to carrier_in.
Note on X6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: from ChatGPT, need revision

## storage
essentials |  |  |  | costs |  |  | constraints
|  |  |  | monetary |  | co2
name | color | parent | carrier | storage_cap | om_annual_investment_fraction | storage_cap | energy_eff | storage_cap_max | energy_cap_per_storage_cap_max | storage_loss | storage_initial | lifetime
li_ion_battery | #c69871 | storage | electricity | 367 | 0.025 | 241.5 | 0.91 | 1000 | 0.25 | 0.001 | 0.5 | 13
tank_35 | #c4d79b | water_tank | heat_35 |  |  |  | 0.96 |  |  | 0.01
tank_60 | #c69871 | water_tank | heat_60 |  |  |  | 0.95 |  |  | 0.015
tank_85 | #e6b8b7 | water_tank | heat_85 |  |  |  | 0.94 |  |  | 0.02
Note on E3: Yiqiao Wang: slope of installation cost curve [$/kWh]
Note on F3: Yiqiao Wang: annual o&m cost relative to the investment cost [1]
Note on H3: Yiqiao Wang: charging/discharging efficiency of conversion technology. Note: the round trip efficiency would be the square of this value!
Note on I3: Yiqiao Wang: [kWh], maximum storage capacity
Note on J3: Yiqiao Wang: relationship between max power and max storage. For example, for a 1kWh li-ion battery, it can handle at maximum 0.25kW of electrical power charging/discharging the battery, which defines this value to 4.
Note on K3: Yiqiao Wang: [1/h], self-discharging rate
Note on M3: Yiqiao Wang: [year]; if no monetary discount is wanted for future years, set the lifetime to 1.
Note on E4: Yiqiao Wang: MANGOret
Note on F4: Yiqiao Wang: MANGOret
Note on H4: Yiqiao Wang: charging/discharging efficiency from MANGOret
Note on E5: Yiqiao Wang: MANGOret
Note on F5: Yiqiao Wang: MANGOret
Note on G5: Yiqiao Wang: 5 from MANGOret and 1.4 from the scaling factor between 2016 and 2022 from ASHP and GSHP

## demand
essentials |  |  |  | constraints
name | color | parent | carrier | resource
demand_electricity | #aeff60 | demand | electricity | df=demand_electricity
demand_space_heating_35 | #fac710 | demand | heat_35 | df=demand_space_heating
demand_space_heating_60 | #fcd510 | demand | heat_60 | df=demand_space_heating
demand_space_heating_85 | #ffa210 | demand | heat_85 | df=demand_space_heating
demand_space_cooling | #12cdd4 | demand | cooling | df=demand_space_cooling
demand_hot_water | #ff6728 | demand | heat_60 | df=demand_hot_water
Note on E4: Yiqiao Wang: in calliope, a dict with key as demand_electricity, value as timeseries df must be input during the initialization of the model.
Note on D5: Yiqiao Wang: might change based on the building's actual emission system.
Note on D6: Yiqiao Wang: might change based on the building's actual emission system.
Note on D7: Yiqiao Wang: might change based on the building's actual emission system.